## Sheet1
FETA Refrigerants List
All information is correct as at |  | 2021-02-08
ALL GWP VALUES ARE AR4
Development Product - not commercially available
Patented Product - only available from supplier noted
ASHRAE provisional designation
PURE PRODUCTS
| Refrigerant | Manufacturer (where applicable) | Trade Name (where applicable) | GWP | ASHRAE | Chemical Name or Components | Composition (%) | Glide(K) | Replaces | Applications
Class
HFC | 23 |  |  | 14800 | A1 | Trifluoromethane | N/A | N/A |  | Ultra low temp refrigeration
| 32 |  |  | 675 | A2L | Difluoromethane | N/A | N/A |  | Blend Component; R410A alternative
| 125 |  |  | 3500 | A1 | Pentafluoroethane | N/A | N/A |  | Blend Component
| 134a |  |  | 1430 | A1 | 1,1,1,2-tetrafluoroethane | N/A | N/A
| 143a |  |  | 4470 | A3 | 1,1,1-trifluoroethane | N/A | N/A |  | Blend Component
| 152a |  |  | 124 | A2 | 1,1-difluoroethane | N/A | N/A
| 227ea |  |  | 3220 | A1 | 1,1,1,2,3,3,3-heptafluoropropane | N/A | N/A
| 236fa |  |  | 9810 | A1 | 1,1,1,3,3,3-hexafluoropropane | N/A | N/A
| 245fa |  |  | 1030 | B1 | 1,1,1,3,3-pentafluoropropane | N/A | N/A
HFO | 1132a |  |  |  | A2L | 1,1 difluoroethene | N/A | N/A |  | Used in R468A/R473A
| 1234yf | Chemours/Honeywell | Opteon™XL10/Solstice®yf | 4 | A2L | 2,3,3,3 tetrafluoroprop-1-ene | N/A | N/A | R134a | Commercial Refrigeration, Chillers
| 1234ze(E) | Honeywell | Solstice®ze | 6 | A2L | trans-1,3,3,3-tetrafluoroprop-1-ene | N/A | N/A | R134a | Commercial Refrigeration, Chillers, Heat Pumps
| 1336mzz(Z) | Chemours | Opteon™mz | 9 | A1 | cis-1,1,1,4,4,4-hexafluorobut-2-ene | N/A | N/A | R123 | Chillers
| 1336mzz(E) | Chemours |  |  | A1 | trans-1,1,1,4,4,4-hexafluorobut-2-ene | N/A
HFCO | 1233zd(E) | Honeywell | Solstice®zd | 4.5 | A1 | trans-1-chloro-3,3,3-trifluoroprop-1-ene | N/A | N/A | R123 | Chillers, HT Heat Pumps
| 1224yd(Z) | AGC | Amolea™yd | 1 | A1 | cis-1-chloro-2,3,3,3-tetrafluoroprop-1-ene | N/A | N/A | R245fa
HCO | 1130(E) |  |  | <25 | B1 | trans-1,2-dichloroethene | N/A | N/A |  | Used in R514A
Others | 13I1 |  |  |  | A1 | Iodotrifluoromethane | N/A | N/A |  | Used in R466A
| E170 |  |  | 1 | A3 | Dimethyl Ether | N/A | N/A
HC | R290 |  |  | 3 | A3 | Propane | N/A | N/A
| R600 |  |  | 4 | A3 | Butane | N/A | N/A
| R600a |  |  | 3 | A3 | Iso butane | N/A | N/A
| R601 |  |  | 4 | A3 | Pentane | N/A | N/A
| R601a |  |  | 4 | A3 | Iso pentane | N/A | N/A
| R1270 |  |  | 2 | A3 | Propene (Propylene) | N/A | N/A
Non fluorocarbon | R717 |  |  | 0 | B2L | Ammonia | N/A | N/A
| R744 |  |  | 1 | A1 | Carbon Dioxide | N/A | N/A
BLENDS
Zeotropes | 404A |  | HP62 | 3922 | A1 | R125/R143a/R134a | 44/52/4 | 0.7
| 407A |  | KLEA 60 | 2107 | A1 | R32/R125/R134a | 20/40/40 | 6.6 | R404A/R507 | LT/MT refrigeration
| 407C |  | KLEA 66/AC9000 | 1774 | A1 | R32/R125/R134a | 23/25/52 | 7.4
| 407F | Honeywell | Performax LT™ | 1825 | A1 | R32/R125/R134a | 30/30/40 | 6.4 | R404A/R507 | LT/MT refrigeration
| 407H | Daikin Chemicals/Koura |  | 1495 | A1 | R32/R125/R134a | 32.5/15/52.5 | 7 | R404A/R507 | LT/MT refrigeration
| 407I | Daikin Chemicals |  | 1459 | A2 | R32/R125/R134a | 19.5/8.5/72
| 410A |  | AZ20 | 2088 | A1 | R32/R125/R134a | 50/50 | <0.2 |  | Chillers, Air Conditioning
| 417A | Chemours | Freon™ MO59 | 2346 | A1 | R125/R134a/R600 | 46.6/50/3.4 | 5.6 | R22 | Air Conditioning, MT refrigeration
| 417B |  |  | 2740 | A1 | R125/R134a/R600 | 79/18.3/2.7 | 3.4
| 417C | ICOR(now owned by Chemours) | Hot Shot 2 | 3268 | A1 | R125/R134a/R600 | 19.5/78.8/1.7 |  | R12/R134a
| 419B |  |  | N/A | A2 | R125/R134a/E170 | 48.5/48/3.5
| 422A | Chemours | Freon™ MO79 | 3143 | A1 | R125/R134a/R600a | 85.1/11.5/3.4 | 2.5 | R22 | LT/MT refrigeration
| 422B | ICOR(now owned by Chemours) | NU-22 | 2526 | A1 | R125/R134a/R600a | 55/42/3 |  | R22
| 422C | ICOR(now owned by Chemours) | One Shot | 3084 | A1 | R125/R134a/R600a | 82/15/3 |  | R404A
| 422D | Chemours | Freon™ MO29 | 2729 | A1 | R125/R134a/R600a | 65.1/31.5/3.4 | 4.5 | R22 | LT/MT refrigeration
| 422E |  |  | N/A | A1 | R125/R134a/R600a | 58/39.3/2.7
| 423A | Chemours | Freon™ 39TC™ | 2280 | A1 | R134a/R227ea | 52.5/47.5 | 5.4 | R12 | Centrifugal chillers
| 424A | Refrigerant Solutions | RS-44 | 2440 | A1 | R125/R134a/R600a/R600/R601a | 50.5/47/0.9/1/0.6 | 4 | R22 | Air Conditioning
| 425A | Sinteco |  | 1505 | A1 | R32/R134a/R227ea | 18.5/69.5/12 | 6.6 | R22/R407C | Air Conditioning, Heat Pumps
| 426A | Refrigerant Solutions | RS-24 | 1508 | A1 | R125/R134a/R600/R601a | 5.1/93/1.3/0.6 | 0.5 | R12 | Refrigeration/MAC
| 427A | Arkema | FX100 | 2138 | A1 |  |  | 7.1 | R22 | Air Conditioning
| 428A | Refrigerant Solutions | RS-52 | 3607 | A1 | R125/R134a/R290/R600a | 77.5/20/0.6/1.9 | 0.5 | R22 | LT refrigeration
| 429A |  |  |  | A3 | R170/R152a/R600 | 60.0/10.0/30.0
| 430A |  |  |  | A3 | R-152a/R600a | 76.0/24.0
431A
432A
433A
| 434A | Refrigerant Solutions | RS-45 | 3245 | A1 | R125/R143a/R134a/R600a | 63.2/18/16/2.8 | 1.5 | R22 | LT refrigeration/Air Conditioing
| 436C |  |  | N/A | A3 | R290/R600a | 95/5 | 2
| 437A | Chemours | Freon™ MO49plus | 1805 | A1 | R125/R134a/R600/R601a | 19.5/78.5/1.4/0.6 | 3 | R12/R401A/R409A | Refrigeration
| 438A | Chemours | Freon™ MO99 | 2265 | A1 | R32/R125/R134a/R600/R601 | 8.5/45/44.2/1.7/0.6 |  | R22 | Refrigeration
| 439A | Sinteco |  | 1983 | A2 | R32/R125/R600a | 50/47/3 | 0.2 | R22/R410A | Air Conditioning, Heat Pumps
| 440A |  |  | 144 | A2 | R290/R134a/R152a | 0.6/1.6/97.8
| 441A | ComStar | HCR 188C1 | 3 | A3 | R170/R290/R600a/R600 | 3.1/54.8/6.0/36.1 | 21.5
| 442A | Refrigerant Solutions | RS-50 | 1888 | A1 | R32/R125/R134a/R152a/R227ea | 31/31/30/3/5 | 4.6 | R404A/R507/R22 | LT/MT refrigeration
| 443A | ComStar | HCR 188C2 | 2 | A3 | R1270/R290/R600a | 55/40/5
| 444A | Koura | AC5 | 88 | A2L | R32/R152a/R1234ze(E) | 12/5/83 |  | R134a | MAC
| 444B | Honeywell | Solstice®L20 | 293 | A2L | R32/R152a/R1234ze(E) | 41.5/10/48.5 | 8 | R22 | Air conditioning (High ambient temp)
| 445A | Koura | AC6 | 130 | A2L | R744/R134a/R1234ze(E) | 6/9/85 |  | R134a | MAC
| 446A | Honeywell |  | 459 | A2L | R32/R1234ze/R600 | 68/29/3 | 5 | R410A | Chillers, Air Conditioning
| 447A | Honeywell | Solstice®L41 | 582 | A2L | R32/R125/R1234ze(E) | 68/3.5/28.5 | 4 | R410A | Chillers, Air Conditioning
| 447B | Honeywell | Solstice®L41z | 739 | A2L | R32/R125/R1234ze(E) | 68/8/24 | 3.5 | R410A | Chillers, Air Conditioning
| 448A | Honeywell | Solstice®N40 | 1386 | A1 | R32/R125/R1234yf/R1234ze(E)/R134a | 26/26/20/21/7 | 6.2 | R404A/R507 | LT/MT refrigeration
| 448B | Honeywell |  | 1321 | A1 | R32/R125/R1234yf/R1234ze(E)/R134a | 21/21/20/31/7 |  | R404A/R508 | LT/MT refrigeration
| 449A | Chemours/Arkema | Opteon™XP40 | 1397 | A1 | R32/R125/R1234yf/R134a | 24.3/24.7/25.3/25.7 | 4.5 | R404A/R507 | LT/MT refrigeration
| 449B | Arkema | ARM-32 | 1411 | A1 | R32/R125/R1234yf/R134a | 25.2/24.3/23.2/27.3 | 5 | R404A/R507 | LT/MT refrigeration
| 449C | Chemours | Opteon™XP20 | 1250 | A1 | R32/R125/R1234yf/R134a | 20/20/31/29 | 7.5 | R407C
| 450A | Honeywell | Solstice®N13 | 601 | A1 | R1234ze(E)/R134a | 58/42 | 0.6 | R134a | MT refrigeration, Chillers, Heat Pumps
| 451A | Inha University, S Korea |  | 147 | A2L | R1234yf/R134a | 89.8/10.2 |  | R134a
| 451B | Inha University, S Korea |  | 161 | A2L | R1234yf/R134a | 88.8/11.2 |  | R134a
| 452A | Chemours/Honeywell | Opteon™ XP44/Solstice®452A | 2140 | A1 | R32/R125/R1234yf | 11/59/30 | 5.4 | R404A/R507 | Transport Refrigeration; Hermetics
| 452B | Chemours/Honeywell | Opteon™XL55/Solstice®L41y | 698 | A2L | R32/R125/R1234yf | 67/7/26 | 1 | R410A | Chillers, Air Conditioning, Heat Pumps
| 452C | Arkema | ARM-35 | 2220 | A1 | R32/R125/R1234yf | 12.5/61/26.5 | 4 | R404A/R507 | Transport Refrigeration; Hermetics
| 453A | Refrigerant Solutions | RS-70 | 1765 | A1 | R32/R125/R134a/R227ea/R600/R601a | 20/20/53.8/5/0.6/0.6 | 4.2 | R404A/R507/R22 | LT refrigeration
| 454A | Chemours | Opteon™ XL40 | 238 | A2L | R32/R1234yf | 35/65 | 5 | R404A/R507 | LT/MT refrigeration
| 454B | Chemours | Opteon™ XL41 | 466 | A2L | R32/R1234yf | 68.9/31.1 | 1.5 | R410A | Chillers, Air Conditioning
| 454C | Chemours | Opteon™ XL20 | 148 | A2L | R32/R1234yf | 21.5/78.5 | 6 | R404A/R507 | LT/MT refrigeration, Heat Pumps
| 455A | Honeywell | Solstice®L40X | 148 | A2L | R744/R32/R1234yf | 3/21.5/75.5 | 8 | R404A/R507, R407C | LT/MT Refrigeration, Heat Pumps
| 456A | Koura | AC5X | 684 | A1 | R32/R134a/R1234ze(E) | 6/45/49 | 4
| 457A | Arkema | ARM-20a | 137 | A2L | R32/R1234yf/R152a | 18/70/12
| 458A | Bluon Energy | TdX20 | 1650 | A1 | R32/R125/R134a/R227ea/R236fa | 20.5/4/61.4/13.5/0.6 | 6.5
| 459A | Arkema | ARM-71a | 459 | A2L | R32/R1234yf/R1234ze(E) | 68/26/6 | 1.5 | R410A
| 459B | Koura | LTR11 | 143 | A2L | R32/R1234yf/R1234ze(E) | 21/69/10 | 8
| 460A | Koura | LTR10 | 2101 | A1 | R32/R125/R134a/R1234ze(E) | 12/52/14/22 | 6
| 460B | Koura | LTR4X | 1350 | A1 | R32/R125/R134a/R1234ze(E) | 28/25/20/27 | 7
| 460C | TRIO GAS |  | 763 | A1 | R32/R125/R134a/R1234ze(E) | 2.5/2.5/46/49
| 461A | Behr Refrigerants |  |  | A1 | R125/R143a/R134a/R227ea/R600a | 55/5/32/5/3 | 5
| 462A | ICOOL Ninghua |  |  | A2 | R32/R125/R143a/R134a/R600 | 9/42/2/44/3 | 6
| 463A | Chemours | Opteon™XP41 | 1493 | A1 | R744/R32/R125/R134a/R1234yf | 6/36/30/14/14 |  | R410A | Refrigeration
| 464A | Refrigerant Solutions | RS100 | 1323 | A1 | R32/R125/R227ea/R1234ze | 27/27/6/40 | 4 | R404A/R507 | LT/MT refrigeration
| 465A | Arkema | ARM25 | 143 | A2L | R32/R290/R1234yf | 21/7.9/71.1 |  | R404A | LT/MT refrigeration
| 466A | Honeywell | Solstice®N41 | 733 | A1 | R32/R125/R13I1 | 49/11.5/39.5 |  | R410A | Air Conditioning
| 467A | SRF, India |  | 1359 | A2L | R32/R125/R134a/R600a | 22/5/72.4/.6 | 7.2 | R407 family/R22
| 468A | Daikin Chemicals |  | <150 | A2L | R1132a/R32/R1234yf | 3.5/21.5/75 | 12.3 | R404A
| 469A | Weiss Technik |  | 1357 | A1 | R744/R32/R125 | 35/32.5/32.5 | Large | R23 | Very low temperature applications
| 470A | Refrigerant Solutions | RS-53 | 977 | A1 | R744/R32/R125/R134a/R1234ze/R227ea | 10/17/19/7/44/3 | 15 | R410A | Air Conditioning
| 470B | Refrigerant Solutions | RS-51 | 749 | A1 | R744/R32/R125/R134a/R1234ze/R227ea | 10/11.5/11.5/3/57/7 | 15 | R404A | LT/MT Refrigeration
| 471A | Honeywell |  | 145 | A1 | R1336mzz(E)/R1234ze/R227ea | 17/78.7/4.3 |  |  | Chillers
| 472A | Angelantoni Climate Technologies |  | 353 | A1 | R744/R32/R134a | 69/12/19 |  | R23 | Very low temperature cascade systems
| 473A | Koura | LFR5 | 1830 | A1 | R744/R1132a/R23/R125 | 60/20/10/10 |  | R23 | Ultra Low Temp refrigeration
Azeotropes | 507 |  | AZ50 | 3985 | A1 | R125/R143a | 50/50 |  |  | LT/MT refrigeration
| 508A |  |  | 13214 | A1 | R23/R116 | 39/61 |  |  | Ultra Low Temp refrigeration
| 508B | Chemours | Suva 95 | 13396 | A1 | R23/R116 | 46/54 |  |  | Ultra Low Temp refrigeration
| 511A |  |  | 5 | A3 | R290/E170 | 95/5
| 512A |  |  | 196 | A2L | R134a/R152a | 5/95
| 513A | Chemours | Opteon™XP10 | 631 | A1 | R1234yf/R134a | 56/44 |  | R134a | Commercial Refrigeration, Chillers, Transport, Heat Pumps
| 513B | Daikin Chemicals |  | 594 | A1 | R1234yf/R134a | 58.5/41.5 |  | R134a | Commercial Refrigeration, Chillers
| 514A | Chemours | Opteon™XP30 | 2 | B1 | R1336mzz(Z)/R1130(E) | 74.7/25.3 |  | R123 | Chillers
| 515A | Honeywell | Solstice® 515A | 387 | A1 | R1234ze(E)/R227ea | 88/12 |  | R134a | Chillers/Heat Pumps
| 515B | Honeywell |  | 293 | A1 | R1234ze(E)/R227ea | 91.1/8.9 |  | R134a
| 516A | Arkema | ARM-42 | 140 | A2L | R1234yf/R134a/R152a | 77.5/8.5/14 |  | R134a
Note on E12: martync: N/A denotes "not available".GWP must be calculated from pure compounds

## Sheet2
|  | 470A |  | 470B
744 | 1 | 10 | 0.1 | 10 | 0.1
32 | 675 | 17 | 114.75 | 11.5 | 77.625
125 | 3500 | 19 | 665 | 11.5 | 402.5
134a | 1430 | 7 | 100.1 | 3 | 42.9
1234ze | 6 | 44 | 2.64 | 57 | 3.42
227ea | 3220 | 3 | 96.6 | 7 | 225.4
|  |  | 979.19 |  | 751.945